## Sheet1
| Command | Description | Requirement |  |  | Display |  | Configuration |  | Type |  |  |  |  | Storage |  |  |  | Operation |  | Access Privilege
[6 empty] | ‘D’ Suffix | ‘D’ Suffix
MIB TABLE |  |  | Telnet | MIB | Modbus | M40 | M50 | Feed | Tap | Alarm | Config | Control | Info | Status | RAM | Flash | FRAM | EEPROM | Get | Set | Monitor | User | Admin | Factory | changed from previous REV | needs addressed
general | REBOOT |  | x
| $REBOOT | Software reset. | [5 empty] | ü | ü |  |  | ü | [9 empty] | ü | ü | ü
general | RAM SIZE |  | x
| $RAM | Get the RAM size in bytes. | [5 empty] | ü | ü |  |  |  | ü | [7 empty] | ü | ü | ü | ü
general | STORE DEFAULTS |  | x
| $PGD | Store the current settings as defaults. | [5 empty] | ü | ü |  | ü | [12 empty] | ü
general | RESET WEB PAGES |  | x
| $RWEB | Revert to default web pages. | [5 empty] | ü | ü |  | ü | [11 empty] | ü | ü
general | HELP |  | x
| $HELP | Get help on commands, print all available commands | [5 empty] | ü | ü |  |  | ü | [8 empty] | ü | ü | ü | ü
general | DISCONNECT |  | x
| $EXIT | Disconnect from the Telnet server. | [9 empty] | ü | [8 empty] | ü | ü | ü | ü
| PRODUCT CONFIGURATION REGISTER |  | x
| $PCR,G | Get Product Configuration (8 hex characters max) | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $PCR,S,YYYYYYYY | Set Product Configuration (YYYYYYYY = 32-bit hexadecimal value) bit 5: Tap or Feed: 0 = Tap, 1 = Feed. bit 8: Optional Display: 0 = No, 1 = Yes. bit 9: LCD or LED Display: 0 = LCD, 1 = LED. bit 12: Has Neutral CT: 0 = No, 1 = Yes. bit 24: Report LAN Parameters as NA: 0 = No, 1 = Yes. bit 29: Secure Protocols (SSL and SSH): 0 = Disabled, 1 = Enabled. bit 30: Modbus RTU: 0 = Disabled, 1 = Enabled. bit 31: Wi-Fi: 0 = Disabled, 1 = Enabled. Note: all undefined bits should be zero. | [21 empty] | ü
| USER CONFIGURATION REGISTER |  | x
| $UCR,G | Get User Configuration (8 hex characters max) | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $UCR,S,YYYYYYYY | Set User Configuration (YYYYYYYY = 32-bit hexadecimal value) bit 0: Meter Mode: 0 = Live, 1 = Demo. bit 4: Power Source: 0 = Delta, 1 = Wye. bit 16: Append Units to SNMP Values: 0 = No, 1 = Yes. bit 17: Modbus Data Type: 0 = Double, 1 = Float. bit 20: Ethernet Ring Mode: 0 = Off, 1 = On. bit 24: BACnet Disable: 0 = No, 1 = Yes. bit 25: BACnet Security Disable: 0 = No, 1 = Yes. bit 29: Secure Protocols (SSL and SSH): 0 = Disabled, 1 = Enabled. Note: all undefined bits should be zero. | [17 empty] | ü |  |  | ü | ü
| DISPLAY CONFIGURATION REGISTER |  | x
| $DCR,G | Get Display Configuration (8 hex characters max) | [6 empty] | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $DCR,S,YYYYYYYY | Set Display Configuration (YYYYYYYY = 32-bit hexadecimal value) bit 0: Display Line to Neutral Voltages. bit 4: Display Line to Line Voltages. bit 8: Display Infeed Line Currents. bit 9: Display Infeed Neutral Current. bit 12: Display Infeed Power Factor (All Phases). Note: all undefined bits should be zero. | [17 empty] | ü |  |  | ü | ü
| SWAP CONFIGURATION REGISTER | X = 1 or 2, Register Number | x
| $SCR,X,G | Get Swap Configuration Register X (8 hex characters max) | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $SCR,X,S,YYYYYYYY | Set Swap Configuration Register 1 (YYYYYYYY = 32-bit hexadecimal value) bit 0: CT1 Polarity Reverse. bit 1: CT2 Polarity Reverse. bit 2: CT3 Polarity Reverse. bit 3: CT4 Polarity Reverse. bit 4: CT5 Polarity Reverse. bit 5: CT6 Polarity Reverse. Set Swap Configuration Register 2 (YYYYYYYY = 32-bit hexadecimal value) bits 0-3: Channel 1 CT Number (1-6 or 0 for no change). bits 4-7: Channel 2 CT Number (1-6 or 0 for no change). bits 8-11: Channel 3 CT Number (1-6 or 0 for no change). bits 12-15: Channel 4 CT Number (1-6 or 0 for no change). bits 16-19: Channel 5 CT Number (1-6 or 0 for no change). bits 20-23: Channel 6 CT Number (1-6 or 0 for no change). Note: all undefined bits must be zero. | [17 empty] | ü |  |  |  | ü
| FACTORY PASSWORD |  | x
| $PWF,G | Get telnet factory login password | [5 empty] | ü | ü | [8 empty] | ü | ü |  |  |  |  | ü
| $PWF,S,YYYYYYY | Set telnet factory login password (15 characters max) | [17 empty] | ü |  |  |  | ü
| ADMIN PASSWORD |  | x
| $PWA,G | Get telnet admin login password | [5 empty] | ü | ü | [8 empty] | ü | ü |  |  |  | ü | ü
| $PWA,S,YYYYYYY | Set telnet admin login password (15 characters max) | [17 empty] | ü |  |  | ü | ü
| USER PASSWORD |  | x | [9 empty] | C
| $PWU,G | Get telnet user login password | [5 empty] | ü | ü | [8 empty] | ü | ü |  |  |  | ü | ü
| $PWU,S,YYYYYYY | Set telnet user login password (15 characters max) | [17 empty] | ü |  |  | ü | ü
Outlet | OUTLET X CONFIGURATION REGISTER | X = Outlet 1,2,3, or 4 | x
| $OCR,X,G | Get Outlet X Configuration (2 hex characters max) | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $OCR,X,S,YY | Set Outlet X Configuration | [21 empty] | ü
| METER DIRECT REGISTER ACCESS | X = 0 or 1, Meter IC Select | x
| $MDRA,X,YYYY,G | Get Meter Register (YYYY = 16-bit hexadecimal register address) | [5 empty] | ü | ü |  | ü | [7 empty] | ü |  |  |  |  | ü
| $MDRA,X,YYYY,ZZZZZZZZ,S | Set Meter Register (ZZZZZZZZ = 32-bit hexadecimal register value) | [21 empty] | ü
general | LED TEST | X = LED 0 or 1; Y = B(BLK), G(GRN), R(RED), Y(YEL) | x
| $LED,X,Y | Test the Front Panel LEDs | [5 empty] | ü | ü |  |  | ü | [11 empty] | ü
| BLINK POWER LED |  | x
| $BLKPWRLED | Increase Power LED blink rate to 5 Hz for 5 seconds | [5 empty] | ü | ü |  |  | ü | [10 empty] | ü | ü
general | ETHERNET RING PRIORITY |  | x
| $RNGPRI,G | Get Ethernet Ring Priority | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $RNGPRI,S, Y | Set Ethernet Ring Priority (Y = 0x00 to 0xFE) | [17 empty] | ü |  |  | ü | ü
general | LCD POWER DOWN TIME |  | x | x | x
| $LCDPDT,G | Get LCD power down time |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $LCDPDT,S, Y | Set LCD power down time (Y = time in seconds, 0 turns off this feature) |  |  |  | ü | [13 empty] | ü |  | ü | ü | ü
general | LCD BACKLIGHT LEVEL |  | x | x | x
| $LCDBL,G | Get lcd backlight level |  |  |  | ü | ü | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $LCDBL,S, Y | Set lcd backlight level (Y = 1 to 10) |  |  |  | ü | ü | [12 empty] | ü |  | ü | ü | ü
general | LCD SLIDESHOW SPEED |  | x | x | x
| $LCDSS,G | Get slideshow speed |  |  |  | ü | ü | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $LCDSS,S, Y | Set slideshow speed (Y = time in seconds) |  |  |  | ü | ü | [12 empty] | ü |  | ü | ü | ü
general | LCD TEST |  | x
| $LCDTS,S,1 | Test the Liquid Crystal Display |  |  |  | ü | ü |  |  |  |  | ü | [11 empty] | ü
general | BUTTON TEST |  | x
| $BTS,G | Get status: 0 = Button test request pending. 1 = Waiting for button 1 to be pressed. 2 = Waiting for button 2 to be pressed. 3 = Waiting for button 3 to be pressed. 4 = Waiting for button 4 to be pressed. 5 = Button test passed. 9 = Button test has not been executed on this unit yet. | [9 empty] | ü | [6 empty] | ü |  |  |  |  | ü
| $BTS,S,0 | Initiates a button test. | x | [20 empty] | ü
general | VENDOR NAME | Factory defined | x | x | x
| $VNAM,G | Get Vendor Name (31 characters max) | [16 empty] | ü |  | ü | ü | ü | ü
general | DEVICE NAME | Character field for the user to store information | x | x | x
| $NAME,G | Get Device Name |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $NAME,S,YYYYYYYYYYYYY | Set Device Name (31 characters max) | [17 empty] | ü |  |  | ü | ü
| DEVICE LOCATION | Character Field for the user to store information | x | x | x
| $DEVLO,G | Get Device Location |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $DEVLO,S,YYYYYYYYYYYYY | Set Device Location (15 characters max) | [17 empty] | ü |  |  | ü | ü
| DEVICE ID | Character Field for the user to store information | x | x | x
| $ID,G | Get Device ID |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $ID,S,YYYYYYYYYYYYY | Set Device ID (23 characters max) | [17 empty] | ü |  |  | ü | ü
| MODEL NUMBER | Factory defined F number | x | x | x
| $MODEL,G | Get Model Number ID | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $MODEL,S,YYYYYYYYYYYYY | Set Model Number ID (15 characters max) | [21 empty] | ü
| SERIAL NUMBER | Factory defined serial number | x | x | x
| $SERIAL,G | Get Meter's Serial Number |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $SERIAL,S,YYYYYYYYYYYYY | Set Meter's Serial Number (15 characters max) | [21 empty] | ü
| PRODUCT SERIAL NUMBER | Factory defined product serial number | x | x | x
| $PSERIAL,G | Get Meter's Product Serial Number |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $PSERIAL,S,YYYYYYYYYYYYY | Set Meter's Product Serial Number (15 characters max) | [21 empty] | ü
| PRODUCT TYPE | Factory defined catalog number | x | x | x
| $TYPE,G | Get Device Type | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $TYPE,S,YYYYYYYYYYYYY | Set Device Type (39 characters max) | [21 empty] | ü
| HARDWARE VERSION | ex: 139-101-0 A | x | x | x
| $HV,G | Get Hardware number and version |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $HV,S,R22276-XXX rev X | Set by factory (19 characters max) | [21 empty] | ü
| FIRMWARE VERSION | ex: R22276-116 v1.45 | x | x | x
| $FV,G | Get Firmware number and version |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  | ü |  |  | ü |  | ü | ü | ü | ü
| $FV,S,XXXXX vX.X.X | Set by firmware upload (19 characters max)
| METER VERSION | ex: V1.20 | x | x | x
| $MV,G | Get meter version |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  | ü |  |  | ü |  | ü | ü | ü | ü
| $MV,S,vX.XX | Set by firmware upload (15 characters max)
| WiFi VERSION | ex: 0x2124a503 | x | x
| $WV,G | Get WiFi version |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  | ü |  |  | ü |  | ü | ü | ü | ü
| $WV,S,vX.XX | Set by firmware upload (15 characters max)
| FIRST ERROR MESSAGE |  | x | x | x
| $ERRF,G | Get first error message | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $ERRF,S,Y | Reset first error message (63 characters max) | [17 empty] | ü |  |  |  | ü
| LAST ERROR MESSAGE |  | x | x | x
| $ERRL,G | Get last error message | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $ERRL,R | Reset last error message (63 characters max) | [17 empty] | ü |  |  |  | ü
| ERROR MESSAGE COUNT |  | x | x | x
| $ERRC,G | Get error count | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $ERRC,R | Reset error count | [17 empty] | ü |  |  |  | ü
| EXCEPTION MESSAGE |  | x
| $EXCM,G | Get exception message | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $EXCM,R | Reset exception message | [17 empty] | ü |  |  |  | ü
| EXCEPTION TASK |  | x
| $EXCTID,G | Get exceptionid | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $EXCTID,R | Reset exception id | [17 empty] | ü |  |  |  | ü
| EXCEPTIONPC |  | x
| $EXCPC,G | Get exception pc | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $EXCPC,R | Reset exception pc | [17 empty] | ü |  |  |  | ü
| CALIBRATION DATE |  | x | x | x
| $CALD,G | Get Calibration Date | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $CALD,S,YYYY-MM-DD | Set Calibration Date (15 characters max) | [21 empty] | ü
| NETWORK STATISTICS |  | x
| $NETSTAT | Get Network Statistics | [16 empty] | ü |  | ü | ü | ü | ü
Ethernet | LAN MAC ADDRESS |  | x | x
| $LANMAC,G | Get LAN MAC Address |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $LANMAC,S,YY:YY:YY:YY:YY:YY | Set LAN MAC Address | [21 empty] | ü
| LAN IP ADDRESS |  | x | x
| $LANIP | Get LAN IP Address |  |  |  | ü |  | ü | ü |  | ü |  |  |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| LAN SUBNET MASK ADDRESS |  | x | x
| $LANMK | Get LAN Subnet Mask Address |  |  |  | ü |  | ü | ü |  | ü |  |  |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| LAN GATEWAY ADDRESS |  | x | x
| $LANGW,G | Get LAN Gateway Address |  |  |  | ü |  | ü | ü |  | ü |  |  |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| LAN DHCP | X = 0 or 1 | x | x
| $LANDHCP,G | Get Status of LAN DHCP Enable | [5 empty] | ü | ü |  |  |  |  | ü |  |  |  | ü | ü |  | ü | ü | ü | ü
| $LANDHCP,S,X | Set Status of LAN DHCP Enable Note: Changes to LAN settings take effect after reboot. | [17 empty] | ü |  |  | ü | ü
| LAN STATIC IP ADDRESS |  | x | x
| $LANSIP,G | Get LAN Static IP Address | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $LANSIP,S,YYY.YYY.YYY.YYY | Set LAN Static IP Address | [17 empty] | ü |  |  | ü | ü
| LAN STATIC SUBNET MASK ADDRESS |  | x | x
| $LANSMK,G | Get LAN Static Subnet Mask Address | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $LANSMK,S,YYY.YYY.YYY.YYY | Set LAN Static Subnet Mask Address | [17 empty] | ü |  |  | ü | ü
| LAN STATIC GATEWAY ADDRESS |  | x | x
| $LANSGW,G | Get LAN Static Gateway Address | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $LANSGW,S,YYY.YYY.YYY.YYY | Set LAN Static Gateway Address | [17 empty] | ü |  |  | ü | ü
WIFI | WLAN MAC ADDRESS |  | x | x
| $WLANMAC | Get WLAN MAC Address |  |  |  | ü |  | ü | ü |  | ü |  |  |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $WLANMAC,S,YY:YY:YY:YY:YY:YY | Set WLAN MAC Address | [21 empty] | ü
| WLAN IP ADDRESS |  | x | x
| $WLANIP | Get WLAN IP Address |  |  |  | ü |  | ü | ü |  | ü |  |  |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| WLAN SUBNET MASK ADDRESS |  | x | x
| $WLANMK | Get WLAN Subnet Mask Address |  |  |  | ü |  | ü | ü |  | ü |  |  |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| WLAN GATEWAY ADDRESS |  | x | x
| $WLANGW | Get WLAN Gateway Address |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| WLAN DHCP | X = 0 or 1 | x | x
| $WLANDHCP,G | Get Status of WLAN DHCP Enable | [5 empty] | ü | ü |  |  |  |  | ü |  |  |  | ü | ü |  | ü | ü | ü | ü
| $WLANDHCP,S,X | Set Status of WLAN DHCP Enable Note: Changes to WLAN settings take effect after reboot. | [17 empty] | ü |  |  | ü | ü
| WLAN STATIC IP ADDRESS |  | x | x
| $WLANSIP,G | Get WLAN Static IP Address | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $WLANSIP,S,YYY.YYY.YYY.YYY | Set WLAN Static IP Address | [17 empty] | ü |  |  | ü | ü
| WLAN STATIC SUBNET MASK ADDRESS |  | x | x
| $WLANSMK,G | Get WLAN Static Subnet Mask Address | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $WLANSMK,S,YYY.YYY.YYY.YYY | Set WLAN Static Subnet Mask Address | [17 empty] | ü |  |  | ü | ü
| WLAN STATIC GATEWAY ADDRESS |  | x | x
| $WLANSGW,G | Get WLAN Static Gateway Address | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $WLANSGW,S,YYY.YYY.YYY.YYY | Set WLAN Static Gateway Address | [17 empty] | ü |  |  | ü | ü
| WLAN SSID |  | x | x
| $WLANSSID,G | Get WLAN SSID | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $WLANSSID,S,YYYY | Set WLAN SSID (YYYY = 1 to 32 Alphanumeric Characters) | [17 empty] | ü |  |  | ü | ü
| WLAN PASSWORD |  | x | x
| $WLANPWD,G | Get WLAN Password | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $WLANPWD,S,YYYY | Set WLAN Password YYYY = Text String wpa2: 8 to 64 Characters wpa: 8 to 64 Characters wep: 10 to 26 Hexadecimal Characters | [17 empty] | ü |  |  | ü | ü
| WLAN FIRMWARE UPGRADE ENABLE BIT |  | x
| $WLANPRG,G | Get WLAN Firmware Upgrade Enable Bit | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $WLANPRG,S,X | Set WLAN Firmware Upgrade Enable Bit (X = 1 to upgrade) | [17 empty] | ü |  |  | ü | ü
| WLAN ENCRYPTION |  | x | x
| $WLANENC,G | Get WLAN Encryption | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $WLANENC,S,YYYY | Set WLAN Encryption YYYY = none, wep, wpa, or wpa2 (lower case text only) | [17 empty] | ü |  |  | ü | ü
| BACNET DEVICE INSTANCE |  | x
| $BDI,G | Get BACnet Device Instance | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $BDI,S,Y | Set BACnet Device Instance (Y = 0 to 4194303) | [17 empty] | ü |  |  | ü | ü
| BACNET UDP PORT |  | x
| $BIPORT,G | Get BACnet UDP Port | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $BIPORT,S,YYYYY | Set BACnet UDP Port (YYYYY = 47808 to 47817) | [17 empty] | ü |  |  | ü | ü
Modbus | BACNET BBMD IP ADDRESS |  | x
| $BBMDIP,G | Get BACnet BBMD IP Address | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $BBMDIP,S,YYY.YYY.YYY.YYY | Set BACnet BBMD IP Address | [17 empty] | ü |  |  | ü | ü
| $BBMDIP,R | Disable Foreign Device Registration (BBMD IP Address is set to 0.0.0.0) | [17 empty] | ü |  |  | ü | ü
| BACNET BBMD REGISTRATION TIME-TO-LIVE |  | x
| $BBMDTTL,G | Get BACnet BBMD Registration Time-To-Live (default = 60 seconds) | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $BBMDTTL,S,Y | Set BACnet BBMD Registration Time-To-Live (Y = 10 to 3600 seconds) | [17 empty] | ü |  |  | ü | ü
| MODBUS M20 BASE ADDRESS |  | x | x | x
| $MODM20BA,G | Get Modbus M20 base address |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $MODM20BA,S,Y | Set Modbus M20 base address (Y: 0 = M4, 1 = M20) Note: Changes to Modbus settings take effect after reboot. M4 mode shifts registers 1-40 to 0-39. M20 mode does not move registers 1-40. | [17 empty] | ü |  |  | ü | ü
| MODBUS SERIAL ADDRESS |  | x | x | x
| $MODSA,G | Get Modbus Serial Address |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $MODSA,S,YYYYY | Set Modbus Serial Address | [17 empty] | ü |  |  | ü | ü
| MODBUS BAUD RATE |  | x | x | x
| $MODBD,G | Get baud rate |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $MODBD,S,YYYYY | Set baud rate (YYYYY = 9600 or 19200) | [17 empty] | ü |  |  | ü | ü
| MODBUS SERIAL STOP BITS |  | x | x | x
| $MODST,G | Get number of stop bits |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $MODST,S,Y | Set number of stop bits (Y: 1 = 1 Stop Bit, 2 = Stop Bits) | [17 empty] | ü |  |  | ü | ü
| MODBUS PARITY |  | x | x | x
| $MODP,G | Get Modbus Parity |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $MODP,S,Y | Set Modbus Parity (Y: 0 = Even, 1 = Odd, 2 = None) Note: If Parity is 0 or 1, Stop Bits is forced to 1 after reboot. | [17 empty] | ü |  |  | ü | ü
| MODBUS FACTORY ACCESS CODE | XXXXX = 0 - 65535 | x
| $MODFAC,G | Get Modbus Factory Access Code |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  |  |  |  | ü
| $MODFAC,S,XXXXX | Set Modbus Factory Access Code (default = 3855 decimal) | [17 empty] | ü |  |  |  | ü
| MODBUS ADMINISTRATOR ACCESS CODE | XXXXX = 0 - 65535 | x
| $MODAAC,G | Get Modbus Administrator Access Code |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  |  |  | ü | ü
| $MODAAC,S,XXXXX | Set Modbus Administrator Access Code (default = 2570 decimal) | [17 empty] | ü |  |  | ü | ü
| MODBUS USER ACCESS CODE | XXXXX = 0 - 65535 | x
| $MODUAC,G | Get Modbus User Access Code |  |  |  | ü |  | ü | ü |  | ü | [6 empty] | ü | ü |  |  |  | ü | ü
| $MODUAC,S,XXXXX | Set Modbus User Access Code (default = 0) | [17 empty] | ü |  |  | ü | ü
SNMP | SNMP TRAP DESTINATION ADDRESS 1 |  | x | x
| $SNMPTD1,G | Get SNMP Trap Destination Address 1 | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $SNMPTD1,S,YYY.YYY.YYY.YYY | Set SNMP Trap Destination Address 1 | [17 empty] | ü |  |  | ü | ü
SNMP | SNMP TRAP DESTINATION ADDRESS 2 |  | x | x
| $SNMPTD2,G | Get SNMP Trap Destination Address 2 | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $SNMPTD2,S,YYY.YYY.YYY.YYY | Set SNMP Trap Destination Address 2 | [17 empty] | ü |  |  | ü | ü
SNMP | SNMP READ COMMUNITY NAME |  | x | x
| $SNMPRCN,G | Get SNMP Read community name | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $SNMPRCN,S,YYYYYYYYY | Set SNMP Read community name | [17 empty] | ü |  |  | ü | ü
SNMP | SNMP WRITE COMMUNITY NAME |  | x | x
| $SNMPWCN,G | Get SNMP Write community name | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $SNMPWCN,S,YYYYYYYYY | Set SNMP Write community name | [17 empty] | ü |  |  | ü | ü
SNMP | SNMP TRAP COMMUNITY NAME |  | x | x
| $SNMPTCN,G | Get SNMP TRAP community name | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $SNMPTCN,S,YYYYYYYYY | Set SNMP TRAP community name | [17 empty] | ü |  |  | ü | ü
| SNMP TRAP ALARM BACKOFF |  | x
| $ALMBACK,G | Get SNMP trap alarm backoff. | [15 empty] | ü | ü |  | ü | ü | ü | ü
| $ALMBACK,S,X | Set SNMP trap alarm backoff in seconds (default = 300). Note: prevents SNMP Trap chatter if a monitored value is bouncing across an alarm threshold. | [15 empty] | ü |  | ü |  |  | ü | ü
Email | EMAIL FROM ADDRESS | ex: noReply@uecorp.com | x | x
| $EMFM,G | Get Email Address | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $EMFM,S,YYYYYYYYYY | Set Email Address | [17 empty] | ü |  |  | ü | ü
| EMAIL TO ADDRESS |  | x | x
| $EMTO,G | Get Email Address | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $EMTO,S,YYYYYYYYYY | Set Email Address | [17 empty] | ü |  |  | ü | ü
| EMAIL SERVER |  | x | x
| $EMSVR,G | Get Server | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $EMSVR,S,YYYYYYYY | Set Server | [17 empty] | ü |  |  | ü | ü
| EMAIL PORT |  | x | x
| $EMPT,G | Get Port | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $EMPT,S,YYYYYYYY | Set Port | [17 empty] | ü |  |  | ü | ü
| EMAIL AUTHENTICATION | Not available, set to 0 ($EMATH,S,0). | x | x
| $EMATH,G | Get Authentication | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $EMATH,S,YYYYYYYY | Set Authentication (Y: 0 = None, 1 = Authentication Required) | [17 empty] | ü |  |  | ü | ü
| EMAIL LOGIN | Not available, set to null string ($EMLOG,R). | x | x
| $EMLOG,G | Get Login | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $EMLOG,S,YYYYYYYY | Set Login | [17 empty] | ü |  |  | ü | ü
| EMAIL PASSWORD | Not available, set to null string ($EMPW,R). | x | x
| $EMPW,G | Get Password | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $EMPW,S,YYYYYYYY | Set Password | [17 empty] | ü |  |  | ü | ü
| EMAIL ALARM HOLDOFF |  | x | x
| $EMAH,G | Get email holdoff. (Email is resent at this interval. Default = 60 seconds.) | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $EMAH,S,Y | Set email holdoff. (Y = Holdoff Time in Seconds) | [17 empty] | ü |  |  | ü | ü
| EMAIL FILE |  | x | x
| $EMFILE,G | Get Emailfile name (Default file stored in web pages as email.txt) | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $EMFILE,S,YYYYYYYY | Set emailfile name | [17 empty] | ü |  |  | ü | ü
SNTP | SNTP SERVER |  | x | x
| $SNTPSVR,G | Get SNTP Server | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $SNTPSVR,S,YYYYYYYY | Set SNTP Server | [17 empty] | ü |  |  | ü | ü
Infeed | LINE TO NEUTRAL VOLTAGE AVERAGE |  | x | x | x
| $LTNVA | Get Line to Neutral Voltage Average | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| LINE TO LINE VOLTAGE AVERAGE |  | x | x | x
| $LTLVA | Get Line to Line Voltage Average | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| INFEED LINE CURRENT AVERAGE |  | x | x | x
| $INFLCA | Get Infeed Line Current Average | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| INFEED LINE CURRENT RATING |  | x | x | x
| $INFLCR,G | Get Infeed Line Current Rating | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $INFLCR,S,YYY | Set Infeed Line Current Rating | [5 empty] | ü | ü | [10 empty] | ü |  |  | ü | ü
| INFEED TOTAL LINE CURRENT DEMAND |  | x | x | x
| $INFCD,G | Infeed Current Demand (uses line current to determine demand) | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFCD,R | Reset Current Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED TOTAL LINE CURRENT PEAK DEMAND |  | x | x | x
| $INFCPD,G | Infeed Current Peak Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFCPD,R | Reset Current Peak Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED DEMAND TIME |  | x | x | x
| $INFDT,G | Get Infeed Demand Interval | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $INFDT,S,YYY | Set Infeed Demand Interval | [17 empty] | ü |  | ü | ü | ü
| INFEED TOTAL ACTIVE POWER |  | x | x | x
| $INFTACP | Get Infeed Total Active Power | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED PEAK TOTAL ACTIVE POWER |  | x | x | x
| $INFPTACP,G | Get Infeed Peak Total Active Power | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFPTACP,R | Reset Infeed Peak Total Active Power | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED TOTAL ACTIVE POWER DEMAND |  | x | x | x
| $INFTACPD,G | Get Infeed Total Active Power Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFTACPD,R | Reset Infeed Total Active Power Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED PEAK TOTAL ACTIVE POWER DEMAND |  | x | x | x
| $INFPTACPD,G | Get Infeed Peak Total Active Power Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFPTACPD,R | Reset Infeed Peak Total Active Power Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED TOTAL REACTIVE POWER |  | x | x | x
| $INFTRACP | Get Infeed Total Reactive Power | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED TOTAL REACTIVE POWER DEMAND |  | x | x | x
| $INFTRACPD,G | Get Infeed Total Reactive Power | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFTRACPD,R | Reset Infeed Total Reactive Power | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED PEAK TOTAL REACTIVE POWER DEMAND |  | x | x | x
| $INFPTRACPD,G | Get Infeed Total Reactive Power | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFPTRACPD,R | Reset Infeed Total Reactive Power | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED TOTAL APPARENT POWER |  | x | x | x
| $INFTAPP | Get Infeed Total Apparent Power | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED TOTAL APPARENT POWER DEMAND |  | x | x | x
| $INFTAPPD,G | Get Infeed Total Apparent Power Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFTAPPD,R | Reset Infeed Total Apparent Power Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED PEAK TOTAL APPARENT POWER DEMAND |  | x | x | x
| $INFPTAPPD,G | Get Infeed Peak Total Apparent Power Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFPTAPPD,R | Reset Infeed Peak Total Apparent Power Demand | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED TOTAL POWER FACTOR |  | x | x | x
| $INFTPF,G | Get Total Power Factor | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED ALARM STATUS |  | x | x | x
| $INFALM,G | Get infeed alarm status | [16 empty] | ü |  | ü | ü | ü | ü
| INFEED MEASURED NEUTRAL CURRENT |  | x | x | x
| $INFMNC | Get the Measured Neutral Current of the Infeed | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| FREQUENCY |  | x | x | x
| $FREQ | Get Frequency | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| LINE TO LINE VOLTAGE |  | x | x | x
| $LLV,A | Get Line to Line Voltage ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $LLV,1 | Get Line to Line Voltage ph1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $LLV,2 | Get Line to Line Voltage ph2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $LLV,3 | Get Line to Line Voltage ph3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED LINE CURRENT |  | x | x | x
| $INFLC,A | Get Infeed Line Current: L1, L2, L3, CalcNeut, MeasNeut | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLC,1 | Get Infeed Line Current Line 1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLC,2 | Get Infeed Line Current Line 2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLC,3 | Get Infeed Line Current Line 3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLC,4 | Get Infeed Line Current Calculated Neutral |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLC,5 | Get Infeed Line Current Measured Neutral |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED LINE CURRENT MINUMUM |  | x | x | x
| $INFLCMN,A,G | Get Infeed Line Current Minimum: L1, L2, L3, CalcNeut, MeasNeut | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMN,A,R | Reset Line1, Line 2, Line 3, Neutral | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCMN,1,G | Get Infeed Line Current Minimum Line 1 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMN,1,R | Reset Line 1 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMN,2,G | Get Infeed Line Current Minimum Line 2 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMN,2,R | Reset Line 2 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMN,3,G | Get Infeed Line Current Minimum Line 3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMN,3,R | Reset Line 3 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMN,4,G | Get Infeed Line Current Maximum Calculated Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMN,4,R | Reset Infeed Line Current Maximum Calculated Neutral | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMN,5,G | Get Infeed Line Current Maximum Measured Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMN,5,R | Reset Infeed Line Current Maximum Measured Neutral | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| INFEED LINE CURRENT MAXIMUM |  | x | x | x
| $INFLCMX,A,G | Get Infeed Line Current Maximum: L1, L2, L3, CalcNeut, MeasNeut | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMX,A,R | Reset Line1, Line 2, Line 3, Neutral | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCMX,1,G | Get Infeed Line Current Maximum Line 1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMX,1,R | Reset Line 1 |  |  |  | ü |  | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMX,2,G | Get Infeed Line Current Maximum Line 2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMX,2,R | Reset Line 2 |  |  |  | ü |  | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMX,3,G | Get Infeed Line Current Maximum Line 3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMX,3,R | Reset Line 3 |  |  |  | ü |  | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMX,4,G | Get Infeed Line Current Maximum Calculated Neutral |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMX,4,R | Reset Infeed Line Current Maximum Calculated Neutral |  |  |  | ü |  | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMX,5,G | Get Infeed Line Current Maximum Measured Neutral |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCMX,5,R | Reset Infeed Line Current Maximum Measured Neutral |  |  |  | ü |  | ü | ü | [10 empty] | ü |  | ü | ü | ü
| INFEED LINE CURRENT RATING % of |  | x | x | x
| $INFLCRP,A | Get Infeed Line Current % of Rated: L1, L2, L3, CalcNeut, MeasNeut | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLCRP,1 | Get Infeed Line Current % of Rated Line 1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLCRP,2 | Get Infeed Line Current % of Rated Line 2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLCRP,3 | Get Infeed Line Current % of Rated Line 3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLCRP,4 | Get Infeed Line Current % of Rated Calculated Neutral |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFLCRP,5 | Get Infeed Line Current % of Rated Measured Neutral |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED LINE CURRENT MIN ALARM |  | x | x | x
| $INFLCMNA,A,G | Get Infeed Line Current Minimum Alarm: L1, L2, L3, CalcNeut, MeasNeut | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMNA,A,S,YYY,YYY,YYY,YYY,YYY | Set All | [6 empty] | ü | ü | [7 empty] | ü |  | ü |  |  | ü | ü
| $INFLCMNA,1,G | Get Infeed Line Current Minimum Alarm Line 1 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMNA,1,S,YYY | Set Line 1 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMNA,2,G | Get Infeed Line Current Minimum Alarm Line 2 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMNA,2,S,YYY | Set Line 2 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMNA,3,G | Get Infeed Line Current Minimum Alarm Line 3 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMNA,3,S,YYY | Set Line 3 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMNA,4,G | Get Infeed Line Current Minimum Alarm Calculated Neutral | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMNA,4,S,YYY | Set Infeed Line Current Minimum Alarm Calculated Neutral | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMNA,5,G | Get Infeed Line Current Minimum Alarm Measured Neutral | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMNA,5,S,YYY | Set Infeed Line Current Minimum Alarm Measured Neutral | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| INFEED LINE CURRENT MAX ALARM |  | x | x | x
| $INFLCMXA,A,G | Get Infeed Line Current Maximum Alarm: L1, L2, L3, CalcNeut, MeasNeut | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMXA,A,S,YYY,YYY,YYY,YYY,YYY | Set All | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMXA,1,G | Get Infeed Line Current Maximum Alarm Line 1 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMXA,1,S,YYY | Set Line 1 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMXA,2,G | Get Infeed Line Current Maximum Alarm Line 2 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMXA,2,S,YYY | Set Line 2 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMXA,3,G | Get Infeed Line Current Maximum Alarm Line 3 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMXA,3,S,YYY | Set Line 3 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMXA,4,G | Get Infeed Line Current Maximum Alarm Calculated Neutral | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMXA,4,S,YYY | Set Infeed Line Current Maximum Alarm Calculated Neutral | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $INFLCMXA,5,G | Get Infeed Line Current Maximum Alarm Measured Neutral | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $INFLCMXA,5,S,YYY | Set Infeed Line Current Maximum Alarm Measured Neutral | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| INFEED LINE CURRENT DEMAND |  | x | x | x
| $INFLCD,A,G | Get Infeed Line Current Demand: L1, L2, L3, CalcNeut, MeasNeut | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCD,A,R | Reset Line1, Line 2, Line 3, (Neutral) | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCD,1,G | Get Infeed Line Current Demand Line 1 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCD,1,R | Reset Line1 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCD,2,G | Get Infeed Line Current Demand Line 2 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCD,2,R | Reset Line 2 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCD,3,G | Get Infeed Line Current Demand Line 3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCD,3,R | Reset Line 3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCD,4,G | Get Infeed Line Current Demand Calculated Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCD,4,R | Reset Infeed Line Current Demand Calculated Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCD,5,G | Get Infeed Line Current Demand Measured Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCD,5,R | Reset Infeed Line Current Demand Measured Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| INFEED LINE CURRENT PEAK DEMAND |  | x | x | x
| $INFLCPD,A,G | Get Infeed Line CurrentPeak Demand: L1, L2, L3, CalcNeut, MeasNeut | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCPD,A,R | Reset Line1, Line 2, Line 3, Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCPD,1,G | Get Infeed Line Current Peak Demand Line 1 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCPD,1,R | Reset Line1 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCPD,2,G | Get Infeed Line Current Peak Demand Line 2 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCPD,2,R | Reset Line 2 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCPD,3,G | Get Infeed Line Current Peak Demand Line 3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCPD,3,R | Reset Line 3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCPD,4,G | Get Infeed Line Current Peak Demand Calculated Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCPD,4,R | Reset Infeed Line Current Peak Demand Calculated Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $INFLCPD,5,G | Get Infeed Line Current Peak Demand Measured Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFLCPD,5,R | Reset Infeed Line Current Peak Demand Measured Neutral | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
Infeed Phase | LINE TO NEUTRAL VOLTAGE |  | x | x | x
| $LNV,A | Get Line to Neutral Voltage ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $LNV,1 | Get Line to Neutral Voltage ph1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $LNV,2 | Get Line to Neutral Voltage ph2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $LNV,3 | Get Line to Neutral Voltage ph3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| LINE TO LINE VOLTAGE MINIMUM |  | x | x | x
| $LLVMN,A,G | Get Line to Line Voltage Minimum ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $LLVMN,A,R | Reset ph1, ph2, ph3 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $LLVMN,1,G | Get Line to Line Voltage Minimum ph1 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $LLVMN,1,R | Reset ph1 | [5 empty] | ü | ü |  |  |  | ü | [6 empty] | ü |  | ü | ü | ü
| $LLVMN,2,G | Get Line to Line Voltage Minimum ph2 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $LLVMN,2,R | Reset ph2 | [5 empty] | ü | ü |  |  |  | ü | [6 empty] | ü |  | ü | ü | ü
| $LLVMN,3,G | Get Line to Line Voltage Minimum ph3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $LLVMN,3,R | Reset ph3 | [5 empty] | ü | ü |  |  |  | ü | [6 empty] | ü |  | ü | ü | ü
| LINE TO LINE VOLTAGE MAXIMUM |  | x | x | x
| $LLVMX,A,G | Get Line to Line Voltage Maximum ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $LLVMX,A,R | Reset ph1, ph2, ph3 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $LLVMX,1,G | Get Line to Line Voltage Maximum ph1 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $LLVMX,1,R | Reset ph1 | [5 empty] | ü | ü |  |  |  | ü | [6 empty] | ü |  | ü | ü | ü
| $LLVMX,2,G | Get Line to Line Voltage Maximum ph2 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $LLVMX,2,R | Reset ph2 | [5 empty] | ü | ü |  |  |  | ü | [6 empty] | ü |  | ü | ü | ü
| $LLVMX,3,G | Get Line to Line Voltage Maximum ph3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $LLVMX,3,R | Reset ph3 | [5 empty] | ü | ü |  |  |  | ü | [6 empty] | ü |  | ü | ü | ü
| LINE TO LINE VOLTAGE MIN ALARM |  | x | x | x
| $LLVMNA,A,G | Get Line to Line Voltage Minimum Alarm ph1, ph2, ph3 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $LLVMNA,A,S,YYY,YYY,YYY | Set ph1, ph2, ph3 | [6 empty] | ü | [10 empty] | ü |  | ü | ü | ü
| $LLVMNA,1,G | Get Line to Line Voltage Minimum Alarm ph1 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $LLVMNA,1,S,YYY | Set ph1 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $LLVMNA,2,G | Get Line to Line Voltage Minimum Alarm ph2 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $LLVMNA,2,S,YYY | Set ph2 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $LLVMNA,3,G | Get Line to Line Voltage Minimum Alarm ph3 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $LLVMNA,3,S,YYY | Set ph3 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| LINE TO LINE VOLTAGE MAX ALARM |  | x | x | x
| $LLVMXA,A,G | Get Line to Line Voltage Maximum Alarm ph1, ph2, ph3 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $LLVMXA,A,S,YYY,YYY,YYY | Set ph1, ph2, ph3 | [6 empty] | ü | [10 empty] | ü |  | ü | ü | ü
| $LLVMXA,1,G | Get Line to Line Voltage Maximum Alarm ph1 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $LLVMXA,1,S,YYY | Set ph1 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $LLVMXA,2,G | Get Line to Line Voltage Maximum Alarm ph2 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $LLVMXA,2,S,YYY | Set ph2 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $LLVMXA,3,G | Get Line to Line Voltage Maximum Alarm ph3 | [5 empty] | ü | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $LLVMXA,3,S,YYY | Set ph3 | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| INFEED POWER FACTOR |  | x | x | x
| $INFPF,A | Get Infeed Power Factor ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFPF,1 | Get Infeed Power Factor ph1 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFPF,2 | Get Infeed Power Factor ph2 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFPF,3 | Get Infeed Power Factor ph3 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED APPARENT POWER |  | x | x | x
| $INFAPP,A | Get Infeed Apparent Power ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFAPP,1 | Get Infeed Apparent Power ph1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFAPP,2 | Get Infeed Apparent Power ph2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFAPP,3 | Get Infeed Apparent Power ph3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED ACTIVE POWER |  | x | x | x
| $INFACP,A | Get Infeed Active Power ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFACP,1 | Get Infeed Active Power ph1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFACP,2 | Get Infeed Active Power ph2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFACP,3 | Get Infeed Active Power ph3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED PEAK ACTIVE POWER |  | x | x | x
| $INFPACP,A | Get Infeed Peak Active Power ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFPACP,1 | Get Infeed Peak Active Power ph1 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFPACP,2 | Get Infeed Peak Active Power ph2 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFPACP,3 | Get Infeed Peak Active Power ph3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| INFEED REACTIVE POWER |  | x | x | x
| $INFRACP,A | Get Infeed Reactive Power ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFRACP,1 | Get Infeed Reactive Power ph1 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFRACP,2 | Get Infeed Reactive Power ph2 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $INFRACP,3 | Get Infeed Reactive Power ph3 | [5 empty] | ü | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| INFEED ENERGY |  | x | x | x
| $INFE,A,G | Get Infeed Energy ph1, ph2, ph3 | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFE,1,G | Get Infeed Energy ph1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFE,2,G | Get Infeed Energy ph2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $INFE,3,G | Get Infeed Energy ph3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
Infeed Line | INFEED TOTAL ENERGY |  | x | x | x
| $INFTE,G | Get Infeed Total Energy | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
Infeed Line | RESET ALL ENERGY VALUES |  | x | x | x
| $ENERGY,R | Reset All Energy Values | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
Infeed Line | ENERGY ACCUMULATORS (for test only) | X = Current Transformer 1,2,3, 4, 5, 6, 7, or 8 | x
| $EACC,X,G | Get Energy Accumulator Value for Current Transformer X | [5 empty] | ü | ü |  |  | ü | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $EACC,A,G | Get Energy Accumulator Value for All Current Transformers | [5 empty] | ü | ü |  |  | ü | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $EACC,X,S,Y | Set Energy Accumulator Value for Current Transformer X | [5 empty] | ü | ü |  |  | ü | ü |  |  |  | ü |  |  | ü |  |  |  | ü
| $EACC,X,R | Reset Energy Accumulator Value for Current Transformer X | [5 empty] | ü | ü |  |  | ü | ü |  |  |  | ü |  |  | ü |  |  |  | ü
| $EACC,A,R | Reset All Energy Accumulators | [5 empty] | ü | ü |  |  | ü | ü |  |  |  | ü |  |  | ü |  |  |  | ü
Outlet | OUTLET X IDENTIFIER | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLID,X,G | Get Outlet X ID | [6 empty] | ü |  |  |  | ü | [5 empty] | ü |  | ü | ü | ü | ü
| $OTLID,X,S,YYYYYYYY | Set Outlet X ID (15 characters max) | [6 empty] | ü |  |  |  | ü | [6 empty] | ü |  |  | ü | ü
| OUTLET ALARM STATUS |  | x | x | x
| $OUTALM,G | Get OUTLET alarm status | [16 empty] | ü |  | ü | ü | ü | ü
| OUTLET X LINE CURRENT | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLLC,X,A | Get Outlet X, Line Current Line 1 , Line 2, Line 3, (Neutral) | [6 empty] | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $OTLLC,X,1 | Get Outlet X, Line Current Line 1 |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $OTLLC,X,2 | Get Outlet X, Line Current Line 2 |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $OTLLC,X,3 | Get Outlet X, Line Current Line 3 |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $OTLLC,X,N | Get Outlet X, Line Current Line N |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| OUTLET X LINE CURRENT RATING | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLLCR,X,G | Get Outlet X Line Current Rating. One rating for each outlet | [6 empty] | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $OTLLCR,X,S,YYY | Set Outlet X Line Current Rating | [6 empty] | ü | [10 empty] | ü |  |  |  | ü
| OUTLET X LINE CURRENT RATING % of | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLLCRP,X,A | Get Outlet X Line Current % of Rated Line 1, Line 2, Line 3, (Neutral) | [6 empty] | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $OTLLCRP,X,1 | Get Outlet X Line Current % of Rated Line 1 |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $OTLLCRP,X,2 | Get Outlet X Line Current % of Rated Line 2 |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $OTLLCRP,X,3 | Get Outlet X Line Current % of Rated Line 3 |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| $OTLLCRP,X,N | Get Outlet X Line Current % of Rated Neutral Conductor |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| OUTLET X LINE CURRENT MINIMUM | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLLCMN,X,A,G | Get Outlet Line Current Minimum Line 1 , Line 2, Line 3, (Neutral) | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMN,X,A,R | Reset Line1, Line 2, Line 3, (Neutral) | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCMN,X,1,G | Get Outlet Line Current Minimum Line 1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMN,X,1,R | Reset Line 1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCMN,X,2,G | Get Outlet Line Current Minimum Line 2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMN,X,2,R | Reset Line 2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCMN,X,3,G | Get Outlet Line Current Minimum Line 3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMN,X,3,R | Reset Line 3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCMN,X,N,G | Get Outlet Line Current Minimum Neutral Conductor |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMN,X,N,R | Reset Neutral |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| OUTLET X LINE CURRENT MAXIMUM | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLLCMX,X,A,G | Get Outlet Line Current Maximum Line 1 , Line 2, Line 3, (Neutral) | [5 empty] | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMX,X,A,R | Reset Line1, Line 2, Line 3, (Neutral) | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCMX,X,1,G | Get Outlet Line Current Maximum Line 1 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMX,X,1,R | Reset Line 1 |  |  |  | ü |  | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $OTLLCMX,X,2,G | Get Outlet Line Current Maximum Line 2 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMX,X,2,R | Reset Line 2 |  |  |  | ü |  | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $OTLLCMX,X,3,G | Get Outlet Line Current Maximum Line 3 |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMX,X,3,R | Reset Line 3 |  |  |  | ü |  | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $OTLLCMX,X,N,G | Get Outlet Line Current Maximum Neutral Conductor |  |  |  | ü |  | ü | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCMX,X,N,R | Reset Neutral |  |  |  | ü |  | ü | ü | [10 empty] | ü |  | ü | ü | ü
| OUTLET CURRENT MIN ALARM | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLCMNA,A,G | Get Current Minimum Alarm for All Outlets | [6 empty] | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $OTLCMNA,A,S,YYY,YYY,YYY,YYY | Set Current Minimum Alarm for All Outlets | [6 empty] | ü | ü | [7 empty] | ü |  | ü |  | ü | ü | ü
| $OTLCMNA,X,G | Get Outlet X Current Minimum Alarm | [6 empty] | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $OTLCMNA,X,S,YYY | Set Outlet X Current Minimum Alarm | [6 empty] | ü | ü | [7 empty] | ü |  | ü |  | ü | ü | ü
| OUTLET CURRENT MAX ALARM | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLCMXA,A,G | Get Current Maximum Alarm for All Outlets | [6 empty] | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $OTLCMXA,A,S,YYY,YYY,YYY,YYY | Set Current Maximum Alarm for All Outlets | [6 empty] | ü | ü | [7 empty] | ü |  | ü |  | ü | ü | ü
| $OTLCMXA,X,G | Get Outlet X Current Maximum Alarm | [6 empty] | ü | ü | [7 empty] | ü | ü |  | ü | ü | ü | ü
| $OTLCMXA,X,S,YYY | Set Outlet X Current Maximum Alarm | [6 empty] | ü | ü | [7 empty] | ü |  | ü |  | ü | ü | ü
| OUTLET X DEMAND TIME | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLDT,X,G | Get Outlet X Demand Time | [6 empty] | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $OTLDT,X,S,YYY | Set Outlet X Demand Time | [17 empty] | ü |  | ü | ü | ü
| OUTLET X TOTAL ACTIVE POWER | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLTACP,X | Get Outlet X Total Active Power |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| OUTLET X PEAK TOTAL ACTIVE POWER | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLPTACP,X | Get Outlet X Peak Total Active Power | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| OUTLET X TOTAL REACTIVE POWER | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLTRACP,X | Get Outlet X Total Reactive Power | [6 empty] | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| OUTLET X TOTAL APPARENT POWER | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLTAPP,X | Get Outlet X Total Apparent Power |  |  |  | ü |  |  | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| OUTLET X TOTAL POWER FACTOR | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLTPF,X,G | Get Outlet X Total Power Factor | [6 empty] | ü |  |  |  | ü |  | ü |  |  |  | ü |  | ü | ü | ü | ü
| OUTLET X TOTAL ENERGY | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLTE,X,G | Get Outlet X Total Energy |  |  |  | ü |  |  | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
Outlet Phase | OUTLET X LINE IDENTIFIER | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLPID,X,1,G | Get Outlet X Line 1 ID | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $OTLPID,X,1,S,YYYYYYYYYY | Set Outlet X Line 1 ID (15 characters max) | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $OTLPID,X,2,G | Get Outlet X Line 2 ID | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $OTLPID,X,2,S,YYYYYYYYYY | Set Outlet X Line 2 ID (15 characters max) | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $OTLPID,X,3,G | Get Outlet X Line 3 ID | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $OTLPID,X,3,S,YYYYYYYYYY | Set Outlet X Line 3 ID (15 characters max) | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| $OTLPID,X,N,G | Get Outlet X Neutral ID | [5 empty] | ü | ü |  |  |  | ü |  |  |  |  | ü | ü |  | ü | ü | ü | ü
| $OTLPID,X,N,S,YYYYYYYYYY | Set Outlet X Neutral ID (15 characters max) | [5 empty] | ü | ü | [10 empty] | ü |  | ü | ü | ü
| OUTLET X LINE CURRENT DEMAND | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLLCD,X,A,G | Get Outlet X Line Current Demand Line 1, Line 2, Line 3, (Neutral) | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCD,X,A,R | Reset Outlet X Line1, Line 2, Line 3, (Neutral) | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCD,X,1,G | Get Outlet X Line Current Demand Line 1 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCD,X,1,R | Reset Outlet X Line1 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCD,X,2,G | Get Outlet X Line Current Demand Line 2 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCD,X,2,R | Reset Outlet X Line 2 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCD,X,3,G | Get Outlet X Line Current Demand Line 3 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCD,X,3,R | Reset Outlet X Line 3 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCD,X,N,G | Get Outlet X Line Current Demand Line Neutral | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCD,X,N,R | Reset Outlet X Neutral | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| OUTLET X LINE CURRENT PEAK DEMAND | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLLCPD,X,A,G | Get Outlet X Line Current Peak Demand Line 1, Line 2, Line 3, (Neutral) | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCPD,X,A,R | Reset Outlet X Line1, Line 2, Line 3, Neutral | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCPD,X,1,G | Get Outlet X Line Current Peak Demand Line 1 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCPD,X,1,R | Reset Outlet X Line1 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCPD,X,2,G | Get Outlet X Line Current Peak Demand Line 2 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCPD,X,2,R | Reset Outlet X Line 2 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCPD,X,3,G | Get Outlet X Line Current Peak Demand Line 3 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCPD,X,3,R | Reset Outlet X Line 3 | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| $OTLLCPD,X,N,G | Get Outlet X Line Current Peak Demand Neutral Conductor | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLLCPD,X,N,R | Reset Outlet X Neutral | [6 empty] | ü |  |  |  | ü |  |  |  | ü |  |  | ü |  | ü | ü | ü
| OUTLET X TOTAL LINE CURRENT DEMAND | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLTLCD,X,G | Get Outlet X Total Line Current Demand |  |  |  | ü |  |  | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLTLCD,X,R | Reset Outlet X Total Line Current Demand | [17 empty] | ü |  | ü | ü | ü
| OUTLET X PEAK TOTAL LINE CURRENT DEMAND | X = Outlet 1,2,3, or 4 | x | x | x
| $OTLTLCPD,X,G | Get Outlet X Peak Total Line Current Demand |  |  |  | ü |  |  | ü |  |  |  | ü |  |  |  | ü |  | ü |  | ü | ü | ü | ü
| $OTLTLCPD,X,R | Reset Outlet X Peak Total Line Current Demand | [17 empty] | ü |  | ü | ü | ü
n/a | CURRENT ZERO THRESHOLD |  | x
| $CZERO,G | Get Current Zero Threshold | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $CZERO,S,YYY | Set Current Zero Threshold (YYY = 0 to 5.0 Amps) | [17 empty] | ü |  |  | ü | ü
n/a | CALIBRATION MAXIMUM VOLTAGE L-N | X = Phase 1,2, or 3 | x
| $CALVNMAX,X,G | Get Calibration Maximum Voltage L-N for Phase X | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $CALVNMAX,X,S,YYYYYY | Set Calibration Maximum Voltage L-N for Phase X | [17 empty] | ü |  |  |  | ü
n/a | CALIBRATION MAXIMUM VOLTAGE L-L | X = Phase 1,2, or 3 | x
| $CALVLMAX,X,G | Get Calibration Maximum Voltage L-L for Phase X | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $CALVLMAX,X,S,YYYYYY | Set Calibration Maximum Voltage L-L for Phase X | [17 empty] | ü |  |  |  | ü
n/a | CALIBRATION MAXIMUM CURRENT | X = Current Transformer 1,2,3, 4, 5, 6, 7, or 8 | x
| $CALIMAX,X,G | Get Calibration Maximum Current for Current Transformer X | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $CALIMAX,X,S,YYYYYY | Set Calibration Maximum Current for Current Transformer X | [17 empty] | ü |  |  |  | ü
n/a | CALIBRATION VOLTAGE GAIN | X = Phase 1,2, or 3 | x
| $CALV,X,G | Get Calibration Voltage Gain for Phase X | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $CALV,X,S | Set Calibration Voltage Gain for Phase X | [17 empty] | ü |  |  |  | ü
n/a | CALIBRATION CURRENT GAIN | X = Current Transformer 1,2,3, 4, 5, 6, 7, or 8 | x
| $CALI,X,G | Get Calibration Current Gain for Current Transformer X | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $CALI,X,S,YYYYYY | Set Calibration Current Gain for Current Transformer X | [17 empty] | ü |  |  |  | ü
n/a | CALIBRATION CURRENT PHASE OFFSET | X = Current Transformer 1,2,3, 4, 5, 6, 7, or 8 | x
| $CALPAI,X,G | Get Calibration Current Phase Offset for Current Transformer X | [5 empty] | ü | ü |  | ü | [6 empty] | ü | ü |  | ü | ü | ü | ü
| $CALPAI,X,S,YYYYYY | Set Calibration Current Phase Offset for Current Transformer X | [17 empty] | ü |  |  |  | ü